# Welsh Islamic Cultural Association Swansea

# Scope and Specification Document

Contract Reference: Sketty Mosque and Community Centre - Renewable Energy Upgrade

Contract Duration: 4 Months

Submission Deadline: 05 November 2025 at 12 noon

Client: Sketty Mosque and Community Centre

Location: Sketty Park Road, Swansea, SA2 9AS

Selection: Only one supplier will be selected

## 1. Project Overview

Welsh Islamic Cultural Association (WICAS) is seeking a qualified contractor for the supply, installation, and commissioning of integrated renewable energy systems at Sketty Mosque & Community Centre. The project includes two separate lots:
Lot 1: ASHP’s with underfloor heating to designated parts of the ground floor and to feed existing back of house radiators and additional radiators that are to be installed on the first floor (Ladies’ Prayer Hall).
Lot 2: Additional Solar PV with battery storage and EV chargers.

Both lots must be delivered as a single, integrated solution by the same contractor. Subcontracting is permitted; however, the main contractor will retain full responsibility for the performance, coordination, and compliance of all subcontracted work. All communication and contractual obligations will remain strictly between WICAS and the appointed contractor.

## 2. Site Information

The site comprises a religious and community facility with kitchen, multi-purpose hall and prayer halls. The existing heating system includes electric air conditioning and a gas boiler. The electric air conditioning is to be left in place to be used as cooling during summer months. The roof is a combination of flat and pitched tiled surfaces suitable for solar installation. Flooring currently comprises carpet to the main prayer halls & vinyl flooring to multipurpose hall and entrance foyer

## 3. Scope of Works

### Lot 1: Air Source Heat Pump & Underfloor Heating System

The contractor shall design, supply, install and commission integrated Air Source Heat Pump (ASHP) systems as follows:

- Main Prayer Hall, ground floor, measuring approximately 142 m², to be served by a 14kw ASHP. Including removal of existing concrete floor, installation of insulation, underfloor heating pipework, manifolds, pumps, buffer tank if required and controls. This space must be divided into two independently controlled zones (50/50 split front and rear).

- Multipurpose Hall, ground floor, approximately 116 m², to be served by a 14kw ASHP. Including removal of existing concrete floor, installation of insulation, underfloor heating pipework, manifolds, pumps, buffer tank if required and controls. This space must be divided into two independently controlled zones (separated by the existing folding partition).

- Front Entrance Lobby, approx. 50 m², to be supplied by the Multipurpose Hall ASHP, with one independently controlled zone. Including removal of existing concrete floor, install insulation, underfloor heating pipework, manifolds, pumps and controls*

- Office, approx. 50 m², to be supplied by the Multipurpose Hall ASHP, with one independently controlled zone. Including removal of existing concrete floor, installation of insulation, underfloor heating pipework, manifolds, pumps and controls*

- Kitchen, rear entrance, male toilets/ablution area existing radiators to ground floor plus female toilet/ablution area existing radiators on the first floor that are currently fed by a gas system boiler in the kitchen shall be linked to a 11.2 kW ASHP via a buffer tank. Logic control required to integrate/manage the two heat sources.

- Ladies Prayer Hall, first floor, install radiator circuits to create two independently controlled zones (separated by existing folding partition), to be fed by the same ASHP as the existing radiators. Size and number of radiators to be determined by BTU requirement based on room volume.

*Should heat-loss calculations/installation configuration demonstrate that an independent circuit is required, a separate 8.5 kW ASHP may be required.

#### Performance Expectations

#### The system must be so designed as to maintain temperatures of 21–23°C in all areas

#### All zone controls must be of Smart technology that can be controlled locally and via an interface/remotely controllable internet application

#### Flooring, Finishes and Reinstatement

#### All carpeted areas are to be carefully uplifted, clearly labelled, and safely stored prior to underfloor heating works. After screed curing, carpets shall be professionally refitted, to the same condition as when lifted. Where laminate or vinyl flooring is removed, it is not to be required to be reinstated; instead, the contractor shall leave all affected subfloors even, sealed, and ready for the client’s future finish. Adjacent finishes, skirtings and thresholds must be protected throughout and reinstated to their original standard upon completion.

Commissioning and Handover

All zones shall undergo full commissioning, including pressure tests, flow-rate balancing, temperature verification and confirmation of control functionality. The contractor shall provide as-built drawings, O&M manuals, commissioning certificates and all manufacturer warranties. Training must be delivered on-site to WICAS staff, covering system operation, scheduling and basic maintenance. All handover documents are to be provided electronically at practical completion.

### Lot 2: Solar PV, Battery Storage & EV Charging

The contractor shall design, supply, install, test and commission a complete renewable energy system comprising solar photovoltaic panels, integrated battery storage and electric vehicle charging points. The system must function as a coordinated and monitored installation that optimises on-site energy generation, storage, and usage within the Sketty Mosque & Community Centre premises.

The available roof surfaces - a combination of flat and pitched tiled areas - shall be fully assessed and utilised to maximise solar generation while ensuring compliance with structural, planning and safety requirements. The installation shall make efficient use of both roof types and integrate seamlessly with the existing two-year-old PV array.

Solar PV Array

The contractor shall supply and install approximately 77 Solar Panel 465 W Tier-1 rated panels, providing an additional capacity of around 35.8 kWp to the existing system. All modules must be high-efficiency, and carry a minimum 25-year performance warranty. Panels must be securely mounted on proprietary racking systems suitable for both flat and pitched roofs, using weather-sealed fixings to maintain roof integrity and prevent water ingress.

String configuration, DC cabling, isolators, optimisers and inverter connections shall be designed to minimise losses and maximise yield, with all electrical works compliant with BS 7671 and MCS installation standards. The contractor shall complete all necessary DNO (G99/G98) applications and secure approval before grid connection.

Battery Storage

A minimum usable capacity of approximately 80kWh is required. The batteries must feature intelligent energy management, allowing charging from solar generation and discharge during high-load or grid-import periods. Battery modules shall be scalable, with appropriate inverters and control interfaces to support future system expansion.

Battery storage must include automatic safety management features (temperature monitoring, fire protection, and over-current protection) and comply with BS EN 61427 standards. Installation shall be within a secure, ventilated location and integrated into the overall monitoring and control platform.

Inverters and Controls

The contractor shall provide hybrid inverters (or multiple inverters) with sufficient total AC capacity to match or exceed the newly installed 35.8 kW array plus existing approx. 12kw array. The system shall automatically manage solar generation, battery charging, and grid export in line with approved DNO permissions. All inverters, control components and switchgear shall be suitably rated, clearly labelled, and installed in accordance with MCS, BS 7671, and manufacturer requirements.

A centralised monitoring and reporting system shall be provided, offering real-time performance data, fault alerts and remote diagnostics. System data shall be accessible through a secure web portal or mobile-app interface, allowing authorised WICAS staff to view generation, consumption, and battery status.

Electric Vehicle (EV) Charging

The contractor shall supply and install three smart 22 kW AC EV chargers equipped with Type 2 connectors and compliant with BS EN 62196 and OLEV requirements. The chargers shall include intelligent load-balancing, scheduled charging capability, and integration with the renewable energy management system, ensuring solar-prioritised charging where feasible.

Each charger must include a built-in energy meter and RFID or app-based access control. Chargers shall be installed in designated parking bays with appropriate cable containment, protective bollards, and signage.

If DC fast chargers (e.g., 50 kW units) are later preferred, a separate DNO load assessment and design variation shall be required before installation.

System Integration and Energy Management

The PV, battery and EV systems must operate as a single coordinated installation. Control logic shall prioritise the use of on-site generated solar energy before drawing from the grid and enable battery discharge to support site loads or EV charging during peak demand.

The contractor shall ensure compatibility with existing site electrical infrastructure, install all required isolation devices and distribution board modifications, and provide metering for generation, consumption, and export (MPAN registration if applicable).

Monitoring software must provide clear dashboards showing generation, storage levels, export data, and EV charger status. Access permissions and data handling shall comply with the UK General Data Protection Regulation (GDPR).

Workmanship, Safety and Commissioning

All installation work shall be neat, secure, and compliant with applicable legislation and standards, including BS 7671, BS EN 14511, BS EN 61427, BS EN 62196, MCS, and the Renewable Energy Consumer Code (RECC).

The contractor must prepare and implement a site-specific Risk Assessment and Method Statement (RAMS) prior to starting work. All operatives must be suitably qualified, hold relevant CSCS cards, and have manufacturer-approved training for the systems installed.

Scaffolding and safe roof access arrangements must comply with the Work at Height Regulations 2005, and all penetrations or fixings through the roof shall be weather-sealed to maintain building integrity.

Commissioning procedures are detailed under Lot 1 and Lot 2.

Handover and Documentation

At practical completion, the contractor shall provide a comprehensive digital handover pack, including:

- As-built drawings and single-line electrical schematics

- Commissioning certificates and DNO approval documents

- Product datasheets, manufacturer warranties and maintenance schedules

- User manuals for the PV, battery and EV systems

- Login credentials and user guidance for the monitoring portal

- Evidence of staff training provided to WICAS representatives

All waste and packaging must be removed from the site, and recyclable materials disposed of in accordance with environmental regulations. The site shall be left clean and tidy upon completion.

Integration and Contractor Responsibility

- Both Lot 1 (Air Source Heat Pump & Underfloor Heating System) and Lot 2 (Solar PV, Battery Storage & EV Charging) shall be delivered as a single, fully integrated renewable-energy solution.

- The appointed contractor will be solely responsible for the overall design, coordination, installation, commissioning, and performance of all systems, ensuring seamless operational compatibility between the heating, solar, battery, and EV-charging elements.

- Where subcontractors are employed, the principal contractor shall retain full responsibility for their work, including adherence to specification, workmanship standards, safety compliance, and performance outcomes.

- Refer to Lot 1 and Lot 2 for system-specific integration requirements. Unified control and monitoring are detailed in Section 5 - Control System.

### 4. Additional Notes:

## Workmanship and Installation Standards

All works under this contract shall be executed to the highest professional standards of workmanship, safety, and compliance. The contractor shall ensure that all installations are neat, secure, and fully compliant with current UK regulations, manufacturer instructions, and recognised industry best practice.

General Installation Requirements

- All electrical works shall comply with BS 7671 – Requirements for Electrical Installations and be carried out by suitably qualified operatives holding relevant certifications (e.g., NICEIC, NAPIT, or equivalent).

- All plumbing and heating works shall conform to WRAS, Building Regulations Part L and G, and the relevant MCS standards for renewable technologies.

- All equipment, materials and components shall be new, of merchantable quality, and installed strictly in accordance with the manufacturer’s recommendations.

- All visible installations (pipework, cabling, containment, ducting, and trunking) shall be neatly aligned, labelled, and securely fixed.

- All penetrations through walls, floors, or roofs shall be fully sealed to maintain the integrity, fire rating, and weatherproofing of the building.

Quality Assurance and Supervision

- The contractor must implement a documented Quality Assurance (QA) procedure, including pre-installation inspections, mid-installation checks, and final snagging inspections before handover.

- A site supervisor qualified in both mechanical and electrical disciplines shall be present during key installation stages to coordinate trades and ensure compliance.

- All workmanship shall be subject to inspection and approval by WICAS or its appointed representative. Any defects or substandard works identified shall be rectified by the contractor within 10 working days of notification, at no additional cost.

- No variation to the approved system design may be made without the written agreement of WICAS.

Operative Competence

- All operatives must hold relevant NVQ Level 2 or 3 qualifications (Plumbing, Electrical Installation, or Renewable Technologies).

- Where manufacturer-specific training is available, installers must hold that accreditation (e.g., Mitsubishi Ecodan, Aiko, or SigenStor certification).

- All operatives must hold valid CSCS cards and evidence of current Health & Safety training.

- Supervisors must be qualified to oversee multi-disciplinary renewable-energy installations.

Workmanship Warranty

- The contractor shall provide a minimum 2-year workmanship warranty covering all installed systems.

- Any faults or defects arising within this period must be rectified promptly and at no cost to WICAS.

- Manufacturer warranties for all major components (e.g., heat pumps, PV panels, batteries, and inverters) must be clearly identified, registered, and transferred to WICAS upon completion.

Finishes, Cleanliness, and Waste Management

- All work areas must be kept clean, safe, and orderly throughout the installation period.

- Protective coverings shall be used to safeguard carpets, skirtings, and finishes in adjacent areas.

- Upon completion, the contractor shall remove all waste, debris, and packaging from site and dispose of it in accordance with the Waste Electrical and Electronic Equipment (WEEE) Regulations and local environmental requirements.

- Recyclable materials shall be separated and disposed of responsibly.

- Carpet reinstatement requirements are detailed under Lot 1 - ASHP and Underfloor Heating System

Documentation and Certification

At completion, the contractor must provide the following documentation to WICAS:

- Commissioning and test certificates for all systems installed.

- Manufacturer product warranties and datasheets.

- Building Control and DNO approvals, where applicable.

- As-built drawings and O&M manuals in digital format.

- Copies of relevant installer accreditations and training certificates.

## 5. Compliance Requirements

All works must comply with relevant UK legislation, industry standards, and local authority requirements. The contractor is responsible for ensuring full compliance throughout the project lifecycle.

#### Regulatory and Technical Compliance

- All installations must meet applicable British Standards (BS) and European Norms (EN), including:

  - BS 7671 – Electrical installations

  - BS EN 14511 – Heat pump performance

  - BS EN 61427 – Battery systems

  - BS EN 62196 – EV charging infrastructure

- Systems must be installed by MCS-certified professionals where applicable.

#### DNO (Distribution Network Operator) Applications

- The contractor is responsible for submitting and managing all necessary applications to the DNO for grid connection of solar PV and EV charging systems.

- WICAS will provide supporting documentation and site access as needed.

#### Data Protection and Smart Systems

- Any smart control systems, monitoring platforms, or cloud-based interfaces must comply with the UK General Data Protection Regulation (GDPR).

- The contractor must ensure:

  - Secure handling of user data

  - Clear user consent procedures

  - Data storage and access protocols that meet GDPR standards

## 6. Health & Safety Requirements

The contractor must comply with all relevant Health & Safety legislation, including but not limited to:

- The Health and Safety at Work Act 1974

- The Construction (Design and Management) Regulations 2015

- Manual Handling Operations Regulations

- Control of Substances Hazardous to Health (COSHH)

- Waste Electrical and Electronic Equipment (WEEE) Directive

Key requirements:

- A site-specific risk assessment and method statement (RAMS) must be submitted and approved prior to commencement of works.

- All operatives must be appropriately trained and qualified for the tasks they undertake.

- The contractor must ensure safe access and egress for building users throughout the project.

- Appropriate signage, barriers, and protective measures must be in place to safeguard the public and staff.

- Any hazardous materials must be handled and disposed of in accordance with legal and environmental standards.

- Fire safety and emergency procedures must be maintained at all times during the works.

## 7. Project Timeline

The contractor is expected to adhere to the following indicative timeline:

- Tender Submission Deadline: tbc

- Contract Award Notification: tbc

- Site Mobilisation & Pre-Start Meeting: [tbc

- Commencement of Works: tbc

- Completion of Works: tbc

- Final Inspection & Handover: tbc

Any deviation from the agreed timeline must be communicated in writing and approved by WICAS. Delays without valid justification may result in penalties or termination of contract.

## 8. Site Visit

To ensure bidders fully understand the scope, site conditions, and installation requirements, a mandatory site visit is required prior to submitting a tender.

#### Site Visit Details

- Location: Sketty Mosque & Community Centre, Sketty Park Road, Sketty, Swansea, SA2 9AS

- Dates Available: request for the date via email to info@skettymosque.org

- Duration: Approximately 1 hour, including Q&A session

#### Attendance Requirements

- Bidders must confirm attendance at least 48 hours in advance via email to info@skettymosque.org

- A maximum of two representatives per bidding organisation may attend.

- Attendance will be recorded and referenced during tender evaluation.

#### Pre-Visit Checklist

All attendees must review and bring the following:

- Copy of the tender specification document

- Questions or clarifications regarding site access, installation zones, or system integration

- PPE (if required for access to plant or roof areas)

- Awareness of planning permission status and DNO responsibilities

- Understanding of carpeted zones and reinstatement requirements

Failure to attend the site visit may result in disqualification from the tender process, unless exceptional circumstances are agreed in writing by WICAS.

## 9. Retention Clause

To ensure quality and accountability, a retention sum of 5% of the total contract value will be withheld by WICAS upon completion of the works.

#### Release Conditions

- The retention will be released after the end of the Defects Liability Period, which shall be 12 months from the date of practical completion.

- Release is subject to:

  - Final inspection and approval of all works by WICAS or its appointed representative

  - Resolution of all identified defects during the liability period

  - Submission of all required documentation, including commissioning certificates, warranties, and user manuals

#### Dispute Resolution

- If retention is withheld due to unresolved defects or non-compliance, the contractor will be notified in writing with a detailed explanation.

- Any disputes regarding the retention release will be addressed through the following steps:

  - Initial resolution meeting between WICAS and the contractor within 10 working days of notification

  - If unresolved, referral to an independent adjudicator or mediator agreed by both parties

  - Final resolution in accordance with the terms of the contract and applicable UK law

## 10. Handover Process

Upon completion of the installation and commissioning of all systems, the contractor must carry out a formal handover process to ensure WICAS staff are fully equipped to operate and maintain the installed equipment.

1. Final Inspection and Sign-Off

- Conduct a joint inspection with WICAS representatives to verify:

  - All systems are fully operational and defect-free

  - All carpets and surfaces have been reinstated and cleaned

  - Site has been cleaned and tidied in accordance with Section 6 - Workmanship and Installation Standards.

  - Address any outstanding snagging items prior to final sign-off

2. Staff Training

- Provide on-site training for designated WICAS staff covering:

  - Operation of heating controls and thermostats

  - Use of solar PV monitoring systems and battery management

  - EV charger operation and scheduling

  - Basic troubleshooting and maintenance routines

- Training must be delivered by qualified personnel and include practical demonstrations

3. System Walkthrough

- Conduct a full walkthrough of installed systems, including:

  - Location and function of key components (e.g., heat pump units, inverters, battery storage)

  - Safety features and emergency shut-off procedures

  - Access points for maintenance and servicing

4. Documentation

- Provide a complete digital handover pack including:

  - Commissioning certificates for all systems

  - Manufacturer warranties and product datasheets

  - User manuals and quick-reference guides

  - Maintenance schedules and service contact details

  - As-built drawings and system schematics (if applicable)

5. Post-Handover Support

- Offer a minimum 2-year post-installation support period, including:

  - Technical assistance

  - Fault response protocol

  - Annual system health checks (if included in maintenance agreement)